## 请填写
Indoor unit |  |  | Low-height Celing Ducted Type
Model Power supply | AC 1φ, 220～240V/50Hz | AVE-05HCFRL | AVE-07HCFRL | AVE-09HCFRL | AVE-12HCFRL | AVE-15HCFRL | AVE-17HCFRL | AVE-19HCFRL | AVE-22HCFRL | AVE-24HCFRL
Nominal Cooling Capacity | kW | 1.7 | 2.2 | 2.8 | 3.6 | 4.5 | 5.0 | 5.6 | 6.3 | 7.1
| kcal/h | 1500 | 1900 | 2400 | 3100 | 3900 | 4300 | 4800 | 5400 | 6100
| Btu/h | 5800 | 7500 | 9600 | 12300 | 15300 | 17100 | 19100 | 21500 | 24200
Nominal Heating Capacity | kW | 1.9 | 2.5 | 3.2 | 4.0 | 5.0 | 5.6 | 6.3 | 7.1 | 8.0
| kcal/h | 1700 | 2100 | 2700 | 3450 | 4300 | 4800 | 5400 | 6100 | 6800
| Btu/h | 6500 | 8500 | 11300 | 13600 | 17100 | 19100 | 21500 | 24200 | 27300
Cooling Power Consumption | kW | 0.05 | 0.05 | 0.07 | 0.07 | 0.08 | 0.08 | 0.10 | 0.12 | 0.12
Heating Power Consumption | kW | 0.05 | 0.05 | 0.07 | 0.07 | 0.08 | 0.08 | 0.10 | 0.12 | 0.12
Cooling Operating Current | A | 0.25 | 0.25 | 0.35 | 0.35 | 0.38 | 0.38 | 0.46 | 0.57 | 0.57
Heating Operating Current | A | 0.25 | 0.25 | 0.35 | 0.35 | 0.38 | 0.38 | 0.46 | 0.57 | 0.57
Noise Level | Sound Pressure-dB(A) | 22/24/29 | 22/24/29 | 23/25/35 | 23/25/35 | 23/25/36 | 23/25/36 | 23/25/35 | 25/26/39 | 25/26/39
Outer Dimensions | H(mm) | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 192
| W(mm) | 700 | 700 | 700 | 700 | 910 | 910 | 1180 | 1180 | 1180
| D(mm) | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447 | 447
Net Weight | kg | 16 | 16 | 17 | 17 | 21 | 21 | 25 | 26 | 26
Air Flow Rate | m3/h | 282/330/420 | 282/330/420 | 288/342/540 | 288/342/540 | 330/378/720 | 330/378/720 | 462/480/810 | 522/558/1080 | 522/558/1080
Motor Power | W | 14 | 14 | 29 | 29 | 35 | 35 | 40 | 60 | 60
Piping Connections |  | Flare-nut Connection(with Flare Nuts)
Liquid Line | mm | Ø6.35 | Ø6.35 | Ø6.35 | Ø6.35 | Ø6.35 | Ø6.35 | Ø6.35 | Ø9.53 | Ø9.53
Gas Line | mm | Ø12.7 | Ø12.7 | Ø12.7 | Ø12.7 | Ø12.7 | Ø12.7 | Ø15.88 | Ø15.88 | Ø15.88
Condensate Drain |  | VP25(Outer Diameter Ø32mm)
Approximate Packing Measurement | m3 | 0.15 | 0.15 | 0.15 | 0.15 | 0.18 | 0.18 | 0.22 | 0.22 | 0.22
External Pressure | Pa | 10(0-10-30)
Note：
1、The nominal cooling capacity and heating capacity are based on following conditions: Cooling Operation Conditions Indoor Air Inlet Temperature:27oC DB(80oF DB),19.0oC WB(66.2oF WB) Outdoor Air Inlet Temperature:35oC DB(95oF DB) Piping Length:7.5 Meters Piping Lift:0 Meter Heating Operation Conditions Indoor Air Inlet Temperature:20oC DB(68oF DB) Outdoor Air Inlet Temperature:7oC DB(45oF DB),6oC WB(43oF WB) |  |  |  |  | 2、The sound pressure level is based on following conditions:1.5m beneath the unit. The above data was mesaured in an anechoic chamber so that reflected sound should be taken into consideration in the field.