## IDU
Specification for indoor unit
Water module model |  |  | AHM-070UXCSAPA3 | AHM-160UXCSAPA3
Power supply |  |  | 1PH，220～240V/50Hz
Heating capacity |  | kW | 7 | 16
Hot water capacity |  | kW | 7 | 16
Power input |  | kW | 0.285(3.285) | 0.285(3.285)
Dimensions | H*W*D | mm | 890×520×320 | 890×520×320
Packing dimensions | H*W*D | mm | 1120×595×462 | 1120×595×462
Weight | Net | kg | 55 | 58
| Gross | kg | 72 | 75
Heat Exchanger |  |  | plate heat exchanger
Heat Exchanger insulation material |  |  | Elastomeric Foam
Hot water temperature | Heating | ℃ | 15 to 55 | 15 to 55
| DHW | ℃ | 25 to 75 | 25 to 75
| Cooling | ℃ | 5 to 25 | 5 to 25
Sound pressure |  | dB(A) | 33 | 33
Sound power |  | dB(A) | 46 | 46
Piping connections | Gas | mm | Φ9.53 | Φ9.53
| Liquid | mm | Φ15.88 | Φ15.88
Water pump | Type |  | DC motor
| Speed |  | Inverter Control
| Power input | w | 100 | 160
Booster heating |  | kW | 3 | 3
Water filter | Diameter perforations | mm | 0.85 | 0.85
| Meterial |  | Hpb59-1 | Hpb59-1
Water circuit | Piping connections diameter | mm | G1-1/4" | G1-1/4"
| Shut off valve |  | Yes | Yes
| Drain valve |  | Yes | Yes
| Safety valve | Bar | 3 | 3
| Air purge valve |  | Yes | Yes
Expansion vessel | Volume | L | 8 | 8
| Max. water pressure | Bar | 3 | 3
`

## 参数表室外机 (hidden)
Specification for outdoor unit
Outdoor unit Model |  |  |  | AHW-050UCSDP | AHW-070UCSDP | AHW-090UCSDP | AHW-120UCSDP | AHW-140UCSEP | AHW-160UCSEP
Indoor unit Model |  |  |  | AHM-070UXCSAPA3 | AHM-070UXCSAPA3 | AHM-160UXCSAPA3 | AHM-160UXCSAPA3 | AHM-160UXCSAPA3 | AHM-160UXCSAPA3
Power supply |  |  |  | 1PH,220~240V/50Hz | 1PH,220~240V/50Hz | 1PH,220~240V/50Hz | 1PH,220~240V/50Hz | 1PH,220~240V/50Hz | 1PH,220~240V/50Hz
Heating(AW35) without axillary heater | Rated Capacity （A 7℃/W 35℃）average |  | kW | 5 | 7 | 9 | 12 | 14 | 16
| Rated Power （A 7℃/W 35℃） |  | kW | 1.45 | 1.5556 | 1.9481 | 2.9268 | 2.8926 | 3.3755
| COP （A 7℃/W 35℃） |  | kW/kW | 3.45 | 4.5 | 4.62 | 4.1 | 4.84 | 4.74
| Heating Capacity（A2℃/W 35℃） cold |  | kW | 4 | 6 | 8 | 11 | 12 | 14
| COP（A2℃/W 35℃） |  | kW/kW | 2.42 | 3.15 | 3.234 | 2.87 | 3.388 | 3.318
| Heating Capacity （A-7℃/W 35℃） |  | kW | 4.8 | 6.5 | 7.2 | 9.9 | 11.2 | 13.5
| COP（A-7℃/W 35℃） |  | kW/kW | 1.73 | 2.25 | 2.31 | 2.05 | 2.42 | 2.37
| Heating Capacity （A14℃/W 35℃）warm |  | kW | 8 | 10 | 12 | 15 | 17 | 19
Heating(AW35) with auxillary heater | Rated Capacity （A 7℃/W 35℃）average |  | kW | 8 | 10 | 12 | 15 | 17 | 19
| Rated Power （A 7℃/W 35℃） |  | kW | 1.45 | 1.5556 | 1.9481 | 2.9268 | 2.8926 | 3.3755
| COP （A 7℃/W 35℃） |  | kW/kW | 5.51 | 6.4286 | 6.16 | 5.125 | 5.8771 | 5.6288
| Heating Capacity（A2℃/W 35℃） cold |  | kW | 7 | 9 | 11 | 14 | 15 | 17
| COP（A2℃/W 35℃） |  | kW/kW | 3.45 | 4.5 | 4.312 | 3.5875 | 4.114 | 3.9401
| Heating Capacity （A-7℃/W 35℃） |  | kW | 4.8 | 6.5 | 7.2 | 9.9 | 11.2 | 13.5
| COP（A-7℃/W 35℃） |  | kW/kW | 1.73 | 2.25 | 2.31 | 2.05 | 2.42 | 2.37
| Heating Capacity （A14℃/W 35℃）warm |  | kW | 11 | 13 | 15 | 18 | 20 | 22
Heating A7/6℃ LWC45℃（DT=5℃） | Heating Capacity |  | kW | 4.5 | 6.2 | 8.1 | 10.8 | 12.5 | 14.8
| COP |  | kW/kW | 2.97 | 3.87 | 3.97 | 3.53 | 3.7 | 3.95
Cooling A35℃ LWE18℃（DT=5℃） | Rated Capacity |  | kW | 4.5 | 6.5 | 8 | 10.5 | 12 | 13.5
| EER |  | kW/kW | 2.3 | 3 | 2.9 | 2.8 | 2.77 | 2.53
Energy Efficiency Grade | Heating（35℃） |  |  | A+ | A+ | A++ | A++ | A++ | A++
Dimensions | H*W*D |  | mm | 800×950×370 | 800×950×370 | 800×950×370 | 800×950×370 | 1380×950×370 | 1380×950×370
Packing dimensions | H*W*D |  | mm | 930×1025×460 | 930×1025×460 | 930×1025×460 | 930×1025×460 | 1477×1025×600 | 1477×1025×600
Operation Ambient Range | Heating |  | ℃ | -20~35 | -20~35 | -20~35 | -20~35 | -20~35 | -20~35
| Domestic Hot Water |  | ℃ | -20~43 | -20~43 | -20~43 | -20~43 | -20~43 | -20~43
| Cooling |  | ℃ | 10~43 | 10~43 | 10~43 | 10~43 | 10~43 | 10~43
Heating | Sound Pressure |  | dB(A) | 50 | 51 | 52 | 54 | 51 | 52
| Sound Power |  | dB(A) | 63 | 64 | 65 | 67 | 65 | 66
Cooling | Sound Pressure |  | dB(A) | 49 | 50 | 51 | 53 | 50 | 51
| Sound Power |  | dB(A) | 62 | 63 | 64 | 66 | 64 | 65
Refrigerent | Type |  | - | R410A | R410A | R410A | R410A | R410A | R410A
| charge |  | kg | 2.3 | 2.3 | 3.05 | 3.05 | 4.9 | 4.9
Heat Exchanger | Form |  | - | 11: Multi-channel Cross Flow Finned Tube
| Piping | Material | - | 11: Brass
|  | Outer Diameter | φmm | 7 | 7 | 7 | 7 | 7 | 7
|  | Number of Rows | - | 2 | 2 | 2.5 | 2.5 | 2 | 2
| Fin | Material | - | 11: Aluminum
|  | Pitch | mm | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| Maximum Operation Pressure |  | MPa | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15
| Maximum Windward Area |  | m2 | 1.5 | 1.5 | 1.96 | 1.96 | 1.35 | 1.35
| Qty. |  | - | 1 | 1 | 1 | 1 | 2 | 2
| Form |  | - | Axial fan | Axial fan | Axial fan | Axial fan | Axial fan | Axial fan
| Qty. |  | - | 1 | 1 | 1 | 1 | 2 | 2
| Outer Diameter |  | φmm | 544 | 544 | 544 | 544 | 544 | 544
| Rotating Speed |  | rpm | 664 | 664 | 780 | 780 | 560+464 | 560+464
| Fan Motor | Nominal Air Volume | m3/min | 64 | 64 | 69 | 69 | 90 | 100
|  | Form | - | 11: Fully Enclosed Waterproof Motor
|  | Start Mode | - | DC start | DC start | DC start | DC start | DC start | DC start
|  | Nominal Output Power | W | 138 | 138 | 138 | 138 | 51+51 | 51+51
|  | Qty. | - | 1 | 1 | 1 | 1 | 2 | 2
|  | Insulation Class | - | bar: 11 to 22
Compressor | Leakage Pressure | Exhaust Pressure | MPa | 4.15 | 4.15 | 4.15 | 4.15 | 4.15 | 4.15
|  | Suction Pressure | MPa | 2.21 | 2.21 | 2.21 | 2.21 | 2.21 | 2.21
| Compressor Motor | Start Mode | - | Variable frequency | Variable frequency | Variable frequency | Variable frequency | Variable frequency | Variable frequency
|  | Number of Poles | - | 4 | 4 | 4 | 4 | 6 | 6
|  | Insulation Class | - | bar: 11 to 22
| Refrigeration Oil | Grade | - | HAF68D1C | HAF68D1C | α68HES-H | α68HES-H | POE 32-3MAF | POE 32-3MAF
|  | Injection Volume | L | 0.88 | 0.88 | 1.65 | 1.65 | 1.18 | 1.18
Notes：Test conditon of heat pump with electrically driven compressor for space heating and cooling based on the EN 14511-2-2011.

## ODU
Specification for outdoor unit
Outdoor unit Model |  |  |  | AHW-070UCSDP | AHW-090UCSDP | AHW-120UCSDP | AHW-140UCSEP | AHW-160UCSEP
Indoor unit Model |  |  |  | AHM-070UXCSAPA3 | AHM-160UXCSAPA3 | AHM-160UXCSAPA3 | AHM-160UXCSAPA3 | AHM-160UXCSAPA3
Power supply |  |  |  | 1PH,220~240V/50Hz | 1PH,220~240V/50Hz | 1PH,220~240V/50Hz | 1PH,220~240V/50Hz | 1PH,220~240V/50Hz
Heating(AW35) without axillary heater | Rated Capacity （A 7℃/W 35℃） |  | kW | 7 | 9 | 12 | 14 | 16
| Rated Power （A 7℃/W 35℃） |  | kW | 1.5556 | 1.9481 | 2.9268 | 2.8926 | 3.3755
| COP （A 7℃/W 35℃） |  | kW/kW | 4.5 | 4.62 | 4.1 | 4.84 | 4.74
| Heating Capacity（A2℃/W 35℃） |  | kW | 6.9 | 8.1 | 11.1 | 14 | 16
| COP（A2℃/W 35℃） |  | kW/kW | 3.54 | 3.234 | 2.94 | 4.11 | 4.64
| Heating Capacity （A-7℃/W 35℃） |  | kW | 6.35 | 7.2 | 9.95 | 14 | 16
| COP（A-7℃/W 35℃） |  | kW/kW | 2.13 | 2.42 | 2.15 | 3.07 | 2.81
Heating(AW35) with auxillary heater | Rated Capacity （A 7℃/W 35℃） |  | kW | 7（+3） | 9（+3） | 12（+3） | 14（+3） | 16（+3）
| Rated Power （A 7℃/W 35℃） |  | kW | 1.56（+3） | 1.95（+3） | 2.93（+3） | 2.89（+3） | 3.38（+3）
| Heating Capacity（A2℃/W 35℃） |  | kW | 6.9（+3） | 8.1（+3） | 11.1（+3） | 14（+3） | 14（+3）
| Heating Capacity （A-7℃/W 35℃） |  | kW | 6.35（+3） | 7.2（+3） | 9.95（+3） | 14（+3） | 14（+3）
Heating A7/6℃ LWC45℃（DT=5℃） | Heating Capacity |  | kW | 6.2 | 8.12 | 10.95 | 14 | 16
| COP |  | kW/kW | 3.52 | 3.78 | 3.5 | 4.7 | 4.43
Cooling A35℃ LWE7℃（DT=5℃） | Rated Capacity |  | kW | 6.5 | 8 | 10.5 | 12 | 13.5
| EER |  | kW/kW | 3 | 2.9 | 2.8 | 2.77 | 2.53
Energy Efficiency Grade | Heating（35℃） |  |  | A+ | A++ | A++ | A++ | A++
Dimensions | H*W*D |  | mm | 800×950×370 | 800×950×370 | 800×950×370 | 1380×950×370 | 1380×950×370
Packing dimensions | H*W*D |  | mm | 930×1025×460 | 930×1025×460 | 930×1025×460 | 1477×1025×600 | 1477×1025×600
Operation Ambient Range | Heating |  | ℃ | -20~35 | -20~35 | -20~35 | -20~35 | -20~35
| Domestic Hot Water |  | ℃ | -20~43 | -20~43 | -20~43 | -20~43 | -20~43
| Cooling |  | ℃ | 10~43 | 10~43 | 10~43 | 10~43 | 10~43
Heating | Sound Pressure |  | dB(A) | 51 | 52 | 54 | 51 | 52
| Sound Power |  | dB(A) | 64 | 65 | 67 | 65 | 66
Cooling | Sound Pressure |  | dB(A) | 50 | 51 | 53 | 50 | 51
| Sound Power |  | dB(A) | 63 | 64 | 66 | 64 | 65
Refrigerent | Type |  | - | R410A | R410A | R410A | R410A | R410A
| charge |  | kg | 2.3 | 3.05 | 3.05 | 4.9 | 4.9
Heat Exchanger | Form |  | -
| Piping | Material | -
|  | Outer Diameter | φmm | 7 | 7 | 7 | 7 | 7
|  | Number of Rows | - | 2 | 2.5 | 2.5 | 2 | 2
| Fin | Material | -
|  | Pitch | mm | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| Maximum Operation Pressure |  | MPa | 4.15 | 4.15 | 4.15 | 4.15 | 4.15
| Maximum Windward Area |  | m2 | 1.5 | 1.96 | 1.96 | 1.35 | 1.35
| Qty. |  | - | 1 | 1 | 1 | 2 | 2
| Form |  | - | Axial fan | Axial fan | Axial fan | Axial fan | Axial fan
| Qty. |  | - | 1 | 1 | 1 | 2 | 2
| Outer Diameter |  | φmm | 544 | 544 | 544 | 544 | 544
| Rotating Speed |  | rpm | 664 | 780 | 780 | 560+464 | 560+464
| Fan Motor | Nominal Air Volume | m3/min | 64 | 69 | 69 | 90 | 100
|  | Form | -
|  | Start Mode | - | DC start | DC start | DC start | DC start | DC start
|  | Nominal Output Power | W | 138 | 138 | 138 | 51+51 | 51+51
|  | Qty. | - | 1 | 1 | 1 | 2 | 2
|  | Insulation Class | - | E | E | E | E | E
Compressor | Leakage Pressure | Exhaust Pressure | MPa | 4.15 | 4.15 | 4.15 | 4.15 | 4.15
|  | Suction Pressure | MPa | 2.21 | 2.21 | 2.21 | 2.21 | 2.21
| Compressor Motor | Start Mode | - | Variable frequency | Variable frequency | Variable frequency | Variable frequency | Variable frequency
|  | Number of Poles | - | 4 | 4 | 4 | 6 | 6
|  | Insulation Class | - | E | E | E | B | B
| Refrigeration Oil | Grade | - | HAF68D1C | α68HES-H | α68HES-H | POE 32-3MAF | POE 32-3MAF
|  | Injection Volume | L | 0.88 | 1.65 | 1.65 | 1.18 | 1.18
Notes：Test conditon of heat pump with electrically driven compressor for space heating and cooling based on the EN 14511-2-2011.