## 请填写
Indoor unit |  |  | Mini 4-Way Cassette Type
Model Power supply | AC 1Ø, 220～240V/50Hz(60Hz) |  | AVC-05HJFA | AVC-07HJFA | AVC-09HJFA | AVC-12HJFA | AVC-15HJFA | AVC-17HJFA | AVC-19HJFA
Nominal Cooling Capacity |  | kW | 1.5 | 2.2 | 2.8 | 3.6 | 4.5 | 5.0 | 5.6
|  | kcal/h | 1300 | 1900 | 2400 | 3100 | 3800 | 4300 | 4800
|  | Btu/h | 5100 | 7480 | 9520 | 12240 | 15300 | 17000 | 19040
Nominal Heating Capacity |  | kW | 2.0 | 2.5 | 3.3 | 4.2 | 5.0 | 5.6 | 6.3
|  | kcal/h | 1700 | 2100 | 2800 | 3600 | 4300 | 4800 | 5400
|  | Btu/h | 6800 | 8500 | 11220 | 14280 | 17000 | 19040 | 21420
Cooling Power Consumption |  | kW | 0.014 | 0.014 | 0.014 | 0.016 | 0.022 | 0.03 | 0.04
Heating Power Consumption |  | kW | 0.014 | 0.014 | 0.014 | 0.016 | 0.022 | 0.03 | 0.04
Cooling Operating Current |  | A | 0.15 | 0.15 | 0.15 | 0.16 | 0.23 | 0.3 | 0.39
Heating Operating Current |  | A | 0.15 | 0.15 | 0.15 | 0.16 | 0.23 | 0.3 | 0.39
Noise Level(Hi/Me/Lo/Slo) | Sound Pressure | dB(A) | 30/29/28/26 | 30/29/28/26 | 32/30/28/26 | 34/32/29/26 | 38/36/31/28 | 42/39/36/31 | 45/42/38/34
Air Flow Rate(Hi/Me/Lo/Slo) |  | m3/h | 430/390/370/335 | 430/390/370/335 | 470/430/390/350 | 490/430/390/350 | 560/524/424/400 | 660/570/524/424 | 750/650/560/480
Motor Power |  | W | 57 | 57 | 57 | 57 | 57 | 57 | 57
Outer Dimensions | H | mm | 215 | 215 | 215 | 215 | 215 | 215 | 215
| W | mm | 570 | 570 | 570 | 570 | 570 | 570 | 570
| D | mm | 570 | 570 | 570 | 570 | 570 | 570 | 570
Net Weight |  | kg | 14.5 | 14.5 | 14.8 | 14.8 | 15.8 | 15.8 | 15.8
Approximate Packing Measurement |  | m3 | 0.14239 | 0.14239 | 0.14239 | 0.14239 | 0.14239 | 0.14239 | 0.14239
Piping Connections |  |  | Flare-nut Connection(with Flare Nuts)
Liquid Line |  | mm | Ø6.35 | Ø6.35 | Ø6.35 | Ø6.35 | Ø6.35 | Ø6.35 | Ø6.35
Gas Line |  | mm | Ø12.7 | Ø12.7 | Ø12.7 | Ø12.7 | Ø12.7 | Ø12.7 | Ø12.7
Condensate Drain |  | mm | Outer Diameter 32
Panel Model |  |  | HPE-D-NK
Cabinet Color |  |  | Neutral White
Outer Dimensions | H | mm | 37 | 37 | 37 | 37 | 37 | 37 | 37
| W | mm | 620 | 620 | 620 | 620 | 620 | 620 | 620
| D | mm | 620 | 620 | 620 | 620 | 620 | 620 | 620
Net Weight |  | kg | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7 | 2.7
Packing Volume |  | m3 | 0.04624 | 0.04624 | 0.04624 | 0.04624 | 0.04624 | 0.04624 | 0.04624
Note：
1、The nominal cooling capacity and heating capacity are based on following conditions: Cooling Operation Conditions Indoor Air Inlet Temperature:27oC DB(80oF DB),19.0oC WB(66.2oF WB) Outdoor Air Inlet Temperature:35oC DB(95oF DB) Piping Length:7.5 Meters Piping Lift:0 Meter Heating Operation Conditions Indoor Air Inlet Temperature:20oC DB(68oF DB) Outdoor Air Inlet Temperature:7oC DB(45oF DB),6oC WB(43oF WB) |  |  |  |  | 2、The sound pressure level is based on following conditions:1.5m beneath the unit. The above data was mesaured in an anechoic chamber so that reflected sound should be taken into consideration in the field.